## DRC system
SL NO. | SYMBOL | MODEL | DESCRIPTION | RULES
LEVITON GMAX DRC SYSTEM |  |  |  | When requirement specified as networked control with DRC system Most commonly used
1 | #VALUE! | DRC07-ED0 | Line Voltage Room Controller | A Line Voltage Room Controller with 0–10V dimming is a device that acts like a smart brain to turn lights ON/OFF and smoothly adjust their brightness based on inputs from sensors and switches. There is usually one Room controller per room. Room controller is mandatory when sensor or control switches is present in DRC system
2 | #VALUE! | DRD07-ED0 | Smart Pack Relay 0-10V Dimmer | To control multipe zone(different group of lights) with 0-10v dimming technology. If there are more than one zone in a room ,apart from room controller additional smartpacks are needed for each extra zones.
3 | #VALUE! | DRC00-0D0 | DRC Power Supply | A DRC Power Supply is a device that provides additional power to control devices like sensors, switches, and controllers to ensure proper and stable operation of the lighting control system. It is used if there is many number of sensors in a single zone. (more than 6 sensors)
4 | #VALUE! | DRD07-ED0 (EM) | Smart Pack Relay 0-10V Dimmer (EM) | A Emergency Smart Pack (EM) is a device that controls emergency lighting fixtures by turning them ON/OFF and adjusting brightness, while ensuring they operate safely during power failures. For each emergency zone , a separate emergency smartpack is needed
5 | #VALUE! | DRD07-ED0 (CR) | Smart Pack Relay - Controlled Receptacles | A Controlled Receptacles Smart Pack is a device that turns power plug points ON/OFF automatically or manually, helping control when equipment connected to them receives power. For each receptacle circuit, a separate receptacle smartpack is needed
6 | #VALUE! | DRD07-ED0 (DY) | Smart Pack Relay - Daylighting | A Daylight Smart Pack is a device that uses photocell sensors to automatically adjust light brightness based on natural daylight levels For each daylight sensor an individual Daylight smartpack is required
7 | #VALUE! | 1,DRKDN-C1W;1,80301-0SW; | Keypad, 1-Button, On/Off | A 1-Button On/Off Keypad is a simple switch that allows you to manually turn lights ON or OFF with a single press. Used when manual control is needed
8 | #VALUE! | 1,DRKDN-C2W;1,80301-0SW; | Keypad, 2-Button, On, Off | A 2-Button On/Off Keypad is a wall control with separate buttons that lets you manually turn lights ON with one button and OFF with another Used when manual control is needed
9 | #VALUE! | 1,DRKDN-C4W;1,80301-0SW; | Keypad, 4-Button, On, Raise, Lower, Off | A 4-Button Keypad (On, Raise, Lower, Off) is a simple wall switch that lets you turn lights ON, turn them OFF, and make them brighter or dimmer using separate buttons. Used when manual control is needed
10 | #VALUE! | 1,DRKDN-C8W;1,80301-0SW; | Keypad, 8-Button, On, Raise, Lower, Off, 1, 2, 3, 4 | A 8-Button Keypad is a wall control that lets you turn lights ON or OFF, make them brighter or dimmer, and control different groups of lights (like rooms or areas) by pressing separate buttons. An 8-button keypad controls multiple zones by assigning each zone to a separate button, so each button controls a different group of lights. Used when manual control is needed
11 |  | TS007-000 | Touch Screen, 7 in | A 7-inch Touch Screen is a wall-mounted smart control panel that allows users to manage and adjust lighting across multiple rooms by selecting preset scenes (like work mode or all-off), where a single touch sends commands to the lighting system to turn lights ON/OFF or dim them to specific levels in different areas simultaneously. Combines multiple functions like ON/OFF , Dimming , Scene control Requires additional Power supply (refer Sl no. 3)
12 | #VALUE! | DRID0-C02 | 2 Analog Input Interface | Analog Input Interface is a device that connects analog sensors to room controllers or smart packs. Whenever there is analog sensors Analog interface(AI) should be provided as per number of room controllers
13 | #VALUE! | OSR15-MCW | Digital Sensor, Multi-Tech, 1500 sq ft, White | Ceiling mount digital occupancy/vacancy sensor integrated with photocell for daylight detection No Analog input interface needed Coverage of 1500 sqft For daylight detection additional Daylight smartpack is needed for each sensor Used in DRC networked system
14 | #VALUE! | OSR05-ICW | Digital Sensor, White | Ceiling mount digital occupancy/vacancy sensor integrated with photocell for daylight detection No Analog input interface needed Coverage of 500 sqft For daylight detection additional Daylight smartpack is needed for each sensor Used in DRC networked system
15 | #VALUE! | OSC20-MWW | Occ Sensor, MT, 2000 sq ft | Ceiling mount Analog occupancy/vacancy sensor Add Analog input interface (refer sl no.12) along with sensors to connect with room controllers Most commonly used sensor because it has maximum coverage of 2000sqft and can be also be adjusted to small coverage and Since it is multi technology (PIR+Ultrasonic), It can also be used individually as PIR or Ultrasonic sensors Used in DRC networked system
16 | #VALUE! | OSC10-MWW | Occ Sensor, MT, 1000 sq ft | Ceiling mount Analog occupancy/vacancy sensor (Multi technology- PIR+ULTRASONIC) Add Analog input interface (refer sl no.12) along with sensors to connect with room controllers Used in DRC networked system
17 | #VALUE! | OSC05-MWW | Occ Sensor, MT, 500 sq ft | Ceiling mount Analog occupancy/vacancy sensor (Multi technology/Dual Technology- PIR+ULTRASONIC) is required. Add Analog input interface (refer sl no.12) along with sensors to connect with room controllers Used in DRC networked system
18 | #VALUE! | OSC20-RMW | Occ Sensor, MT, 2000 sq ft, HVAC Relay | Ceiling mount Analog occupancy/vacancy sensor with HVAC control (Multi technology/Dual Technology- PIR+ULTRASONIC) is required. Add Analog input interface (refer sl no.12) along with sensors to connect with room controllers Used in DRC networked system
19 | #VALUE! | OSC10-RMW | Occ Sensor, MT, 1000 sq ft, HVAC Relay | Ceiling mount Analog occupancy/vacancy with HVAC control (Multi technology/Dual Technology- PIR+ULTRASONIC) is required. Add Analog input interface (refer sl no.12) along with sensors to connect with room controllers Used in DRC networked system
20 | #VALUE! | OSC20-U0W | Occ Sensor, US, 2000 sq ft | Ceiling mount Analog occupancy/vacancy sensor (ULTRASONIC technology) is required. Add Analog input interface (refer sl no.12) along with sensors to connect with room controllers Used in DRC networked system
21 | #VALUE! | OSC10-U0W | Occ Sensor, US, 1000 sq ft | Ceiling mount Analog occupancy/vacancy (ULTRASONIC technology) is required. Add Analog input interface (refer sl no.12) along with sensors to connect with room controllers Used in DRC networked system
22 | #VALUE! | OSC05-U0W | Occ Sensor, US, 500 sq ft | Ceiling mount Analog occupancy/vacancy (ULTRASONIC technology) is required. Add Analog input interface (refer sl no.12) along with sensors to connect with room controllers Used in DRC networked system
23 | #VALUE! | OSWWV-I0W | Occ Sensor, PIR, Wide View, Wall Mount | wall mount Analog occupancy/vacancy sensor (PIR) . Add Analog interface along with sensors to connect with room controllers Used in DRC networked system
24 | #VALUE! | OSW12-M0W | Occ Sensor, MT, 1200 sq ft, Wall Mount | wall mount Analog occupancy/vacancy sensor (PIR+ULTRASOUND). Add Analog interface along with sensors to connect with room controllers Used in DRC networked system
25 | #VALUE! | OSFHP-ILW | Occ Sensor, PIR, High Bay | Ceiling mount Analog occupancy/vacancy (Ultra sound) is required with ceiling height > 20ft. Add Analog interface along with sensors to connect with room controllers Used in DRC networked system
26 | #VALUE! | PCIND-000 | Photocell, Indoor | Ceiling mount Analog photocell sensor is required for daylight detection in indoor spaces. Add Analog interface along with sensors to connect with room controllers Used in DRC networked system
27 | #VALUE! | 1,01221-2KL;1,84071-040; | Key Switch, Maintained | A Key Switch (Maintained) is a secure switch operated with a key that stays in its selected position (ON or OFF) and is typically used in areas like restrooms and corridors to keep lights or systems continuously ON or OFF until the key is turned again.
28 | #VALUE! | 1,01223-2KL;1,84071-040; | Key Switch, Maintained, 3-way | A Key Switch (Maintained, 3‑Way) is a key-operated switch that stays in its selected position (ON or OFF) and can control the same lights or system from two different locations, commonly used in areas like restrooms and corridors for secure and continuous control.
29 | #VALUE! | 1,01224-2KL;1,84071-040; | Key Switch, Maintained, 4-way | A Key Switch (Maintained, 4‑Way) is a key-operated switch that stays in its selected position (ON or OFF) and allows control of the same lights or system from multiple locations (more than two), making it ideal for areas like corridors and large spaces where control is needed from different points.
30 | #VALUE! | TS004-00W | DRC Touch Screen, White | A 4-inch Touch Screen is a wall-mounted smart control panel that allows users to manage and adjust lighting in single room by selecting preset scenes (like work mode or all-off), where a single touch sends commands to the lighting system to turn lights ON/OFF or dim them to specific levels in different areas simultaneously. Combines multiple functions like ON/OFF , Dimming , Scene control
31 | #VALUE! | ODC0P-00W | Photocell | Ceiling mount Analog photocell sensor is required for daylight detection. Add Analog interface along with sensors to connect with room controllers Used in DRC networked system